## 61853-1 & 2
Module technology | mono-crystalline silicon
Measured by SUPSI PVLab
Contact person | gabi.friesen@supsi.ch
| Power Rating | [5 empty] | Temperature coefficients |  |  | Spectral response |  |  | Angular response |  |  | Thermal properties
| meas. accord. IEC 60904-1/IEC 61853-1 | [5 empty] | meas. accord. IEC 61215 |  |  | measured accord. IEC 60904-8/ IEC 61853-2 |  |  | measured accord. IEC 61853-2 |  |  | measured accord. IEC 61853-2
| Pm[W] | [5 empty] | rel. Isc coeff. | rel. Voc coeff. | rel. Pmax coeff. | Wavelength | Rel. SR |  | AoI | IAM |  | u0 | u1 | NMOT
Irradiance [W/m²]\ Temperature [°C] | 15 | 25 | 50 | 75 | u% [k=2] |  | α [%/°C] | β [%/°C] | δ [%/°C] | nm |  | u% [k=2] | ° |  | u% [k=2] | [Wm^-2 K^-1] | [W m^-3 s K^-1] | [°C]
1100 |  | 313.3421 | 280.7361 | 247.6367 | 1.6% |  | 0.046 | -0.2848 | -0.405 | 311 | 0.027803 | 9.428% | 0 | 1 | 1% | 29.84 | 3.44 | 44.04
1000 | 297.0822 | 285.6859 | 256.75 | 227.7908 | 1.6% | u% [k=2] | 34.35% | 7.795% | 7.852% | 341 | 0.06997 | 9.428% | 1 | 0.99936 | 1.2%
800 | 238.2846 | 229.4387 | 207.019 | 184.2068 | 1.6% |  |  |  |  | 365 | 0.13644 | 9.428% | 20 | 0.99935 | 1.2%
600 | 178.5162 | 172.1169 | 155.8914 | 139.3686 | 1.6% |  |  |  |  | 380 | 0.22832 | 8.521% | 30 | 0.99757 | 1.2%
400 | 118.1365 | 114.0004 | 103.5117 |  | 1.6% |  |  |  |  | 399 | 0.29108 | 6.379% | 40 | 0.99868 | 1.2%
200 | 57.743 | 55.7059 |  |  | 1.6% |  |  |  |  | 418 | 0.316 | 6.387% | 50 | 0.98464 | 1.3%
100 | 28.0205 | 26.9885 |  |  | 2.6% |  |  |  |  | 440 | 0.3281 | 6.803% | 60 | 0.95886 | 1.5%
[10 empty] | 470 | 0.35469 | 6.904% | 65 | 0.92851 | 1.7%
| Isc[A] | [8 empty] | 491 | 0.37654 | 7.264% | 70 | 0.87899 | 1.9%
Irradiance [W/m²]\ Temperature [°C] | 15 | 25 | 50 | 75 | [5 empty] | 499 | 0.38733 | 7.18% | 75 | 0.77947 | 2.4%
1100 |  | 10.4345 | 10.5507 | 10.6637 | 1.5% |  |  |  |  | 530 | 0.41458 | 6.627% | 80 | 0.63328 | 3.4%
1000 | 9.4443 | 9.4868 | 9.5979 | 9.7079 | 1.5% |  |  |  |  | 549 | 0.43308 | 7.434% | 85 | 0.3994 | 6.6%
800 | 7.5577 | 7.5898 | 7.6725 | 7.7563 | 1.5% |  |  |  |  | 570 | 0.44799 | 7.072%
600 | 5.6682 | 5.6924 | 5.754 | 5.8175 | 1.5% |  |  |  |  | 589 | 0.45986 | 7.012%
400 | 3.7786 | 3.7948 | 3.8362 |  | 1.5% |  |  |  |  | 639 | 0.50789 | 6.912%
200 | 1.8889 | 1.8968 |  |  | 1.5% |  |  |  |  | 661 | 0.5212 | 6.725%
100 | 0.94403 | 0.94851 |  |  | 2.5% |  |  |  |  | 698 | 0.55148 | 6.892%
[10 empty] | 749 | 0.58526 | 7.342%
| Voc[A] | [8 empty] | 765 | 0.5926 | 7.278%
Irradiance [W/m²]\ Temperature [°C] | 15 | 25 | 50 | 75 | [5 empty] | 799 | 0.62185 | 7.707%
1100 |  | 39.8986 | 37.0801 | 34.2616 | 0.4% |  |  |  |  | 849 | 0.65377 | 6.93%
1000 | 40.8466 | 39.7147 | 36.8851 | 34.0505 | 0.4% |  |  |  |  | 881 | 0.67532 | 6.874%
800 | 40.4314 | 39.2864 | 36.424 | 33.5616 | 0.4% |  |  |  |  | 899 | 0.65606 | 8.937%
600 | 39.8999 | 38.7388 | 35.836 | 32.9331 | 0.4% |  |  |  |  | 947 | 0.6658 | 9.514%
400 | 39.1605 | 37.9761 | 35.015 |  | 0.4% |  |  |  |  | 999 | 0.62607 | 10.15%
200 | 37.9237 | 36.6981 |  |  | 0.4% |  |  |  |  | 1049 | 0.46908 | 12.57%
100 | 36.7232 | 35.4546 |  |  | 0.4% |  |  |  |  | 1098 | 0.26601 | 21.2%
[10 empty] | 1145 | 0.066234 | 21.6%
[10 empty] | 1198 | 0.0023966 | 23.45%